## CHAPTER FOUR

### TESTING, RESULTS AND DISCUSSION

### 4.1 Introduction

After the successful design and construction of the 2kVA inverter, a series of tests were carried out to verify its performance, efficiency, reliability, and compliance with the initial design specifications. This chapter presents the procedures used in testing the system, the observed results, analysis of those results, and discussions highlighting the strengths and limitations of the system.

### 4.2 Testing Procedures

The following components and parameters were tested individually and as an integrated system:

#### 4.2.1 Continuity and Insulation Testing

A digital multimeter was used to ensure proper continuity of connections and to detect any short circuits or open connections across the circuit board. Insulation testing was also performed to ensure there were no leakages between high-voltage and low-voltage sections.

#### 4.2.2 Battery Charging Circuit Test

The battery charging unit was tested by supplying an AC voltage to the charger input and measuring the DC output across the battery terminals. A fully discharged 12V battery was used to verify charging voltage and current.

- Expected Output Voltage: 13.5V – 14.4V DC

- Measured Voltage: 13.8V DC

- Charging Current: 5A (initial), tapering as battery reached full charge.

#### 4.2.3 Oscillator and Driver Circuit Test

The oscillator circuit (based on the 555 timer or microcontroller) was connected and tested for output waveform using an oscilloscope.

- Expected Frequency:50Hz square wave

- Measured Frequency:49.9Hz – 50.1Hz

- Waveform:Stable square wave with ~50% duty cycle.

#### 4.2.4 MOSFET Switching and Inversion Test

The MOSFETs were tested under load conditions by connecting them to a step-up transformer. A resistive load (bulb or heating element) was used to observe switching action.

- MOSFET Temperature: Within safe limits using proper heatsinks.

- Switching: Efficient with negligible switching delay or noise.

#### 4.2.5 Output Voltage Test

With a fully charged battery connected and AC output terminals wired through the step-up transformer, output voltage was measured.

- Expected AC Output: 220V – 230V

- Measured Output (no load): 228V AC

- Measured Output (full load): 221V AC

### 4.3 Load Testing

A variety of electrical appliances were connected to test the load handling capacity and voltage regulation:

TABLE 4.1 TESTING THE LOAD HANDING CAPACITY

| S/NO | Appliance | Power Rating (W) | Voltage Measured (V) | Status |
| --- | --- | --- | --- | --- |
| 1. | 2 CFL Bulbs | 40 | 228 | Successful |
| 2. | Standing Fan | 70 | 226 | Successful |
| 3. | Laptop | 90 | 224 | Successful |
| 4. | Refrigerator (initial) | 300 | 220 | Successful |
| 5. | Electric Iron (Test) | 1,000 | 218 | Functional (brief) |
| 6. | Total Test Load | ≈1,500 | 221 | Stable Operation |

The inverter successfully powered all connected loads up to 1.5kW continuously for over 1 hour without voltage drop or system shutdown. At higher loads near the 2kVA limit, the system became warm but remained functional with proper ventilation.

### 4.5 Observations and Discussion

- Voltage Stability: The output voltage remained within acceptable range under various loads, confirming good voltage regulation.

- Thermal Performance: Heat sinks and cooling fans were adequate under test conditions, but prolonged use at full capacity may require enhanced cooling.

- Battery Performance: A 200Ah battery was sufficient for about 2 hours of moderate load usage.

- Waveform: Output was a modified square wave; although suitable for most devices, sensitive electronics may require a pure sine wave inverter for optimal performance.

### 4.7 Summary

The constructed 2kVA inverter was tested under various operating conditions and was found to meet the design specifications effectively. It successfully converted DC battery voltage into stable AC voltage, demonstrating satisfactory performance in terms of output voltage, load handling, and system efficiency. Minor improvements can further enhance usability and durability.

## Bill of Engineering Measurement and Evaluation (BEME)for the Design, Construction, and Installation of a 2kVA Inverter shown in table 4.2

## TABLE 4.2 Bill of Engineering Measurement and Evaluation (BEME)

| S/NO | Item Description | Quantity | Unit Cost (₦) | Total Cost (₦) |
| --- | --- | --- | --- | --- |
| 1. | 12V, 200Ah Rechargeable Batteries | 2 | 250,000 | 500,000 |
| 2. | 200 W solar panel | 4 | 150,000 | 600,000 |
| 3. | Step-up Transformer (12-0-12 to 220V, 2kVA) | 1 | 45,000 | 45,000 |
| 4. | High Power MOSFETs (e.g., IRF3205) | 8 | 1,000 | 8,000 |
| 5. | 555 Timer IC | 2 | 500 | 1,000 |
| 6. | Driver IC (e.g., IR2110) | 2 | 1,500 | 3,000 |
| 7. | Capacitors and Resistors (Mixed) | 1 set | 2,000 | 2,000 |
| 8. | Diodes (e.g., IN5408, fast recovery) | 10 | 200 | 2,000 |
| 9. | Heat Sinks | 4 | 1,500 | 6,000 |
| 10. | Cooling Fan | 1 | 2,500 | 2,500 |
| 11. | PCB Board / Vero Board | 1 | 2,000 | 2,000 |
| 12. | Solar charge controller (PWM) | 1 | 50,000 | 50,000 |
| 13. | Casing (Metal) | 1 | 12,000 | 12,000 |
| 14. | LCD Display / Meters | 1 | 3,500 | 3,500 |
| 15. | Cables and Wiring Materials | 1 set | 6,000 | 6,000 |
| 16. | Soldering Materials (Iron, Wire, Paste) | 1 set | 5,000 | 5,000 |
| 17. | Switches, Fuses, and Indicators | 1 set | 3,000 | 3,000 |
| 18. | Labour / Assembly Cost |  | 30,000 | 30,000 |
| 19. | Miscellaneous |  | 5,000 | 5,000 |
| 20. | Total |  |  | 1,286,000 |