CHAPTER FOUR

4.0	RESULTS AND DISCUSSION

4.1	Installation Outcome Overview

The hybridinverter system was successfully installed and configured using the selected components:

- A 4.2kVA hybrid inverter (48V DC input)

- Six (6) monocrystalline 350W solar panels (total: 2,100W)

- Eight (8) 12V, 200Ah deep-cycle batteries (configured in 4S2P for 48V, 400Ah total)

- A 60A MPPT charge controller

- AC/DC protective devices including breakers and surge arresters

All wiring was carried out in compliance with Nigerian and IEC standards using fire-rated, color-coded cables. The installation provided both power reliability and system safety.

4.2	Load Support Capability

The system was designed to handle an estimated peak load of around 950 watts and a daily energy demand of approximately 6.1 kWh. The connected appliances included:

- 10 LED bulbs (10W each)

- 4 ceiling fans (75W each)

- 1 refrigerator (200W)

- 1 television (100W)

- 1 laptop (60W)

- 1 Wi-Fi modem/router (15W)

Upon testing, the inverter seamlessly handled all connected loads without any tripping or voltage instability. The power factor remained near unity, and voltage regulation was consistently within the AC standard range of 228.7V to 230.1V, both at idle and under full load conditions.

#### 4.3	Inverter Performance

The inverter operated seamlessly during the test period, handling inductive and resistive loads without tripping or audible distortion.

- No-load voltage: 230.1V AC

- Full-load voltage: 228.7V AC

- Inverter efficiency: Measured at 93.8%, consistent with manufacturer specs

Voltage regulation remained stable, with minimal fluctuation despite switching surges from inductive appliances like ceiling fans and refrigerators.

Fig. 4.1:Inverter Display Panel (Live readings)

### 4.4 Battery Autonomy and Runtime

With a total usable storage of ~8.2 kWh(48V × 400Ah × 0.5 DOD × 0.85 efficiency), the system provided up to 30 hours of backup under moderate load conditions (≤200W continuous).

Table 4.1: Sample Load Runtime Scenarios

| Load Type | Power (W) | Runtime (hours) | Notes |
| --- | --- | --- | --- |
| Lighting only | 100 | ~48 hrs | LED bulbs only |
| Light + Fan | 400 | ~20 hrs | Fan on for 8–10 hrs/day |
| Light + TV + Fridge | 850 | ~8.5 hrs | Mixed load during blackout |

Battery voltage recovery after partial discharge was observed to be within 2 hours under full solar charging conditions on clear days.

### 4.5 Solar Charging Efficiency

Solar panels were tested during the peak sunlight window of 10 a.m. – 2 p.m. using a digital clamp meter and inverter telemetry.

Peak solar output: 1950–2040W
Daily energy harvested: 7.5 – 8.5 kWh on sunny days
Average charge current: 36–45A via MPPT

The MPPT charge controller operated at ~97% tracking efficiency. Even under cloudy conditions, the system achieved 40–50% of nominal output, thanks to monocrystalline panels' superior low-light performance (Parida et al., 2011).

### 4.6 System Stability and Load Handling

The system underwent simulated worst-case tests, including:

- Simultaneous startup of all loads

- Sudden disconnection of PV input

- Battery-only operation during blackout

### 4.6 User Experience and Monitoring

The hybrid inverter system was equipped with a mobile app (via Wi-Fi) for real-time monitoring of:

- PV input voltage/current

- Battery voltage/state of charge

- Load power consumption

- Error logs

Users reported:

- High satisfaction with quiet operation

- Ease of use through app interface

- Improved quality of life, especially during night-time blackouts

### 4.7 Comparative Analysis with Generator Use

A comparison was made between the solar hybrid system and a previously used 2.5kVA petrol generator.

Table 4.2: Comparative Metrics

| Metric | Solar Hybrid System | Generator (Petrol) |
| --- | --- | --- |
| Fuel cost/month | ₦0 | ₦24,000+ |
| Noise level | Silent | 70–85 dB |
| Emissions | None | CO₂, NOx, PM |
| Maintenance frequency | Monthly check | Weekly service |
| Operating time | 24/7 (sun + battery) | 2–4 hrs/day max |

Result: The solar hybrid system saved over ₦290,000 annually, with zero fuel or emissions.

### 4.8	Challenges Observed

Despite the system's success, certain limitations and challenges were noted:

- Solar performance dipped significantly during three consecutive rainy days

- Battery bank took longer to recharge (~1.5 days after full discharge)

- Initial installation cost remained a financial barrier for lower-income households

Mitigating these would require:

- Adding a secondary energy source (grid or wind)

- Implementing battery bank expansion

- Government subsidies for residential solar adoption

### 4.11 Economic Viability and Payback Period

Installation cost = ~₦1.9 million
Monthly generator cost saved = ~₦24,000
Payback period = ₦1,900,000 / ₦24,000 ≈ 6.6 years

Considering battery replacement every 4–5 years and inflation, the system remains economically viable over a 10-year horizon.

4.12	Bill of Engineering Measurement and Evaluation (BEME)

#### Table 4.3: Bill of Engineering Measurement and Evaluation (BEME)

| S/N | Component/Item Description | Qty | UnitPrice (₦) | TotalCost (₦) |
| --- | --- | --- | --- | --- |
| 1 | 4.2kVA Hybrid Inverter (48V, Pure Sine Wave) | 1 | 450,000 | 450,000 |
| 2 | 12V, 200Ah Deep-Cycle Lead-Acid Batteries | 4 | 150,000 | 600,000 |
| 3 | 350W Monocrystalline Solar Panels | 6 | 85,000 | 510,000 |
| 4 | MPPT Charge Controller (60A, 48V) | 1 | 80,000 | 80,000 |
| 5 | AC/DC Circuit Breakers & Fuse Blocks | Various | Lump Sum | 50,000 |
| 6 | Battery Rack and Ventilated Housing Unit | 1 | 30,000 | 30,000 |
| 7 | Cables (DC/AC, Conduit, Lugs & Connectors) | Various | Lump Sum | 70,000 |
| 8 | Solar Panel Mounting Structure & Clamps | 1 Set | 60,000 | 60,000 |
| 9 | Earthing & Surge Protection Devices (SPD) | 1 Set | 40,000 | 40,000 |
| 10 | System Monitoring (Wi-Fi Dongle/App Setup) | 1 | 20,000 | 20,000 |
| 11 | Installation Labor (Full system integration) | - | Lump Sum | 80,000 |
| 12 | Testing & Commissioning Tools/Consumables | - | Lump Sum | 30,000 |

Total Estimated Cost₦2,020,000