### DESIGN AND CONSTRUCTION OF A 3KVA INVERTER USING 24VOLTZ BATTERY

### BY

### SALAUDEEN ABDULRASHEED OLAMILEKAN

HND/23/SLT/FT/0953

SUBMITTED TO:

DEPARTMENT OF SCIENCE LABORATORY TECHNOLOGY

(PHYSICS UNIT), INSTITUTE OF APPLIED SCIENCES (IAS),

KWARA STATE POLYTECHNIC, ILORIN.

IN PARTIAL FULFILMENT OF THE REQUIREMENTS FOR THE AWARD OF HIGHER NATIONAL DIPLOMA (HND)

IN SCIENCE LABORATORY TECHNOLOGY (SLT)

SUPERVISED BY:

MR. AGBOOLA A. O.

2024/2025 SESSION

CERTIFICATION

This is to certify that this project work has been written by SALAUDEEN ABDULRASHEED OLAMILEKAN with matric number HND/23/SLT/FT/0953 and has been read and approved as meeting the parts of the requirements for the award of Higher National Diploma (HND) in Science Laboratory technology Department, Institute of Applied Sciences, Kwara State Polytechnic.

_____________________________			___________________

MR. AGBOOLA A. O.					DATE

(Project Supervisor)

_____________________________			___________________

DR.USMAN A.					DATE

(Head of Department)

_____________________________			___________________

MR.SALAHU BASHIR 				DATE

(Head of Unit)

- __________________________                          __________________

- (External examiner)                                      DATE

- i

- DEDICATION

This project work is sincerely dedicated to Almighty Allah for His mercy and blessings upon my life and my parents who have solemnly give the full encouragement both financially, Mentally,Physically and words of advices, thanks for your guardians. May Almighty Allah rewarded you abundantly.

ii

ACKNOWLEDGEMENT

All praise is due to Almighty Allah, the Beneficent, the Most Merciful, for His immense support, grace, and the gift of life. I thank Him sincerely for granting me the privilege and strength to begin and complete this project. He is the Giver of knowledge, wisdom, and understanding, and without His guidance, this achievement would not have been possible.

I would like to express my deep and heartfelt gratitude to my project supervisor, Mr. Agboola A. O.  for his consistent support, guidance, and constructive criticism throughout this project. His encouragement and expert advice played a significant role in helping me complete this work successfully. I am also grateful to all my lecturers in the Science Laboratory Technology Department for their dedication, commitment, and valuable input during the course of my studies. May Almighty Allah reward and favor you all abundantly, and may He continue to bless you and your families.

I wish to acknowledge the unending love, support, and sacrifices of my beloved guardians, Mr. and Mrs. Salaudeen From the day I was born up until this stage of my academic journey, you have stood by me morally, financially, and spiritually. Your care and devotion mean the world to me, and I pray that Almighty Allah grants you long life, good health, and the opportunity to enjoy the fruits of your labor. May His blessings be upon you always. Ameen.

iii

TABLE OF CONTENTS

Title Page                                                                                                                                i

Certification                                                                                                                            ii

Dedication                                                                                                                              iii

Acknowledgement                                                                                                                iv

Table of Content                                                                                                                    v

Abstract                                                                                                                                  vi

CHAPTER ONE

1.0	Introduction

1.1 	Background of the study

1.2	Objectives of the project

1.3	Significance of the project

1.4	Scope of the project

1.5	Limitations of the project

CHAPTER TWO

2.0	Literature review

2.1	Overview of Inverter project

2.2	Types of Inverters

2.3	Power Electronics Components in Inverters

2.5	Battery Technology for Inverters

2.6	 Efficiency and Performance Considerations

iv

CHAPTER THREE

3.0	Methodology

3.1	Materials

3.2	Circuit Diagram of the Inverter

3.3	Working Principle of the Inverter

CHAPTER FOUR

4.0	System construction and testing

4.1	Testing and evaluation under load condition

4.2	Power Rating

4.3	Design Specifications (modified sine-wave inverter)

4.4	Challenges encountered

4.5	Protection and safety features

CHAPTER FIVE

5.0	Results, conclusion, and recommendations

5.1	Summary of Findings

5.2	Conclusion

5.3	Recommendations for Improvement

5.4	Future Work

REFERENCES

APPENDICES

v

ABSTRACT

This project focuses on the design and construction of a 3KVA solar inverter system using a 24V battery bank to provide an alternative and reliable source of electricity, especially in areas with unstable or no access to the national grid. The inverter system converts direct current (DC) from solar-charged batteries into alternating current (AC), which can be used to power common household appliances. The design involves key stages such as component selection, circuit design, simulation, physical construction, and performance testing. The system includes protection features such as overload, short-circuit, and low battery shutdown to ensure safe and reliable operation. Testing showed that the inverter successfully produced a stable 220V AC output at 50Hz and performed well under various load conditions. This project demonstrates the possibility of developing a cost-effective, environmentally friendly, and efficient solar power solution for domestic and small-scale commercial applications.

vi

CHAPTER ONE

1.0	INTRODUCTION

Electric power is very important in our daily lives. It is used in homes, offices, schools, and industries to run electrical appliances and machines. Unfortunately, in many areas, the power supply from the national grid is not reliable. This causes problems for people who need electricity to carry out their daily activities. To solve this problem, alternative power sources like generators, solar systems, and inverters are used, (Aremu et,al. 2019). An inverter is an electronic device that changes direct current (DC) from a battery into alternating current (AC), which is the type of electricity used in most homes and businesses. Inverters are quiet, clean, and easy to maintain compared to fuel generators. This project is focused on the design and construction of a 3KVA inverter using a 24-volt battery. A 3KVA inverter is powerful enough to run several home or office appliances like fans, lights, TVs, and small refrigerators. The use of a 24V battery system helps improve performance and reduce power loss. The aim of this project is to build an efficient inverter that can provide backup electricity during power outages. The inverter will include safety features such as overload protection and low battery cutoff. It will also be made using affordable and easily available components to keep the cost low. This project will help in learning how inverter systems work and how they can be used to solve power problems in our communities.

1.1	BACKGROUND OF THE STUDY

In today’s world, electrical energy plays a vital role in economic and technological advancement. The increasing demand for electricity has led to various innovations aimed at ensuring a steady and reliable power supply. However, in many developing regions, irregularities in the power supply from the national grid have necessitated the development of alternative power solutions such as inverters, generators, and solar power systems. Among these alternatives, inverters stand out as one of the most efficient and environmentally friendly means of providing backup power.

An inverter is an electronic device that converts direct current (DC) from a power source, such as a battery, into alternating current (AC), which is used to power household and industrial appliances. The efficiency of an inverter is determined by its design, conversion capability, and battery management system. The design and construction of a 3kVA inverter using a 24V battery system is significant due to its ability to supply sufficient power for small-scale applications while maintaining efficiency, cost-effectiveness, and reliability.

1.2	OBJECTIVES OF THE STUDY

The primary objective of this study is to design and construct a 3kVA inverter using a 24V battery system. Specifically, the project seeks to:

- Develop an efficient inverter circuit capable of converting 24V DC to 220V AC with minimal losses.

- Design a pure sine wave output to ensure compatibility with sensitive electrical appliances.

- Incorporate protective measures such as overload protection, short circuit protection, and thermal management.

- Evaluate the performance of the inverter in terms of efficiency, power output, and reliability.

- Provide an affordable and durable alternative to conventional power backup systems.

1.3	SIGNIFICANCE OF THE STUDY

The significance of this study lies in its potential contribution to solving power-related challenges. A 3kVA inverter can power essential household appliances, small offices, and businesses during power outages, thus reducing reliance on costly and environmentally hazardous alternatives like diesel generators. This study also contributes to the growing body of knowledge on power electronics, particularly in the development of cost-effective and efficient inverters. Additionally, this project serves as a foundation for further research into improved inverter technology with higher efficiency and sustainability.

1.4	SCOPE OF THE PROJECT

This study focuses on the design and construction of a 3kVA inverter using a 24V battery system. It covers the following key

- Constructions of inverter capable of powering appliances below 3kVA voltage.

- Design of a DC to AC inverter using suitable electronics.

- Construction, testing, and evaluation of the inverter system.

However, the study does not include:

- Integration with renewable energy sources such as solar panels.

- Large-scale commercial inverter design.

- Advanced digital control techniques such as microcontroller-based switching.

1.5	LIMITATIONS OF THE PROJECT

While this study aims to develop a reliable and efficient 3kVA inverter, certain limitations may arise, including:

- Component Availability: High-efficiency power electronic components may not be readily available, affecting design choices.

- Cost Constraints: Budget limitations may influence the quality and specifications of components used.

- Testing Environment: The inverter will be tested under controlled conditions, and real-world performance may vary depending on external factors such as battery quality and load variations.

- Heat Dissipation: Managing heat generation in power electronic devices is crucial, and improper cooling mechanisms could impact performance and durability.

CHAPTER TWO

2.0	LITERATURE REVIEW

2.1	OVERVIEW OF INVERTER TECHNOLOGY

Inverters are devices that convert direct current (DC) into alternating current (AC), a crucial process for integrating renewable energy sources and powering household appliances. Early inverters used mechanical switching systems, but with advances in semiconductor technology, modern inverters are more efficient, reliable, and compact. Inverters are key to applications such as solar power systems, uninterruptible power supplies (UPS), and electric vehicles (Hassan et al., 2020).

Modern inverters use high-speed semiconductor switches like MOSFETs (Metal-Oxide-Semiconductor Field-Effect Transistors) and IGBTs (Insulated-Gate Bipolar Transistors), which enable greater energy conversion efficiency and reduced system size. Pulse Width Modulation (PWM) and Maximum Power Point Tracking (MPPT) are two critical techniques used to optimize the operation of inverters in renewable energy applications (Yang et al., 2019).

Key innovations in inverter technology include hybrid inverters (which integrate energy storage and energy generation) and smart inverters capable of grid communication and self-diagnostics (Lee & Kim, 2021). These developments have expanded the versatility and functionality of inverters in modern power systems.

2.2	Types of Inverters

Inverters are categorized based on the waveform they generate, and their applications can range from basic household needs to large industrial setups. The primary types are:

Square Wave Inverters: The simplest type, generating a distorted waveform. Square wave inverters are less efficient and incompatible with many electronic devices but are still used for low-cost applications like basic lighting systems (Smith, 2018).

Modified Sine Wave Inverters: These produce a stepped waveform, offering better efficiency than square wave inverters. Modified sine wave inverters are suitable for many household appliances, though some sensitive electronics may still experience issues (Jones et al., 2020).

Pure Sine Wave Inverters: These inverters produce a smooth, sinusoidal waveform, making them compatible with all appliances, including sensitive devices. They are widely used in residential and industrial settings (Patel & Singh, 2021).

Additional inverter types include:

Centralized Inverters: Typically used in large-scale solar power plants.

Micro inverters: Used in distributed generation systems, where each inverter is attached to an individual solar panel (Huang & Wei, 2019).

2.4	POWER ELECTRONIC COMPONENTS IN INVERTERS

The efficiency of an inverter is determined by its internal power electronic components. Semiconductor devices, including MOSFETs and IGBTs, serve as the core switching elements, controlling the flow of power through the system. Their speed and thermal characteristics are critical for inverter performance (Singh et al., 2019).

Other components that impact inverter efficiency include filter circuits (capacitors and inductors) used to reduce harmonics and smooth the AC output. Additionally, cooling systems such as heat sinks, fan cooling, and liquid cooling are essential to maintain optimal temperature levels and prevent component failure.

Control circuits based on digital signal processors (DSP) or microcontrollers monitor the inverter's performance in real-time, adjusting parameters like voltage and frequency to optimize energy conversion (Kumar & Reddy, 2018).

2.5 Battery Technology for Inverters

Battery technology is a key consideration in inverter design, affecting the overall performance and longevity of energy storage systems.

Lead-Acid Batteries: While low-cost, lead-acid batteries have a limited lifespan and lower energy density compared to newer technologies. They are still commonly used in off-grid applications (Brown & Lee, 2019).

Lithium-Ion Batteries: These batteries are favored for modern inverter systems due to their high energy density, long lifespan, and minimal maintenance requirements. They have become the industry standard for high-performance off-grid and hybrid systems (Kumar & Reddy, 2021).

Flow Batteries: These batteries, while more expensive, offer scalable energy storage and longer lifespans, making them suitable for grid energy storage and large-scale systems (Rani 2020). The charge/discharge rate and efficiency of batteries have a significant impact on inverter performance, with lithium-ion batteries being the most efficient for frequent cycling.

2.6	Efficiency and Performance Considerations

The efficiency of inverters depends on several factors, such as switching losses, thermal management, and total harmonic distortion (THD).

Switching Losses: Research by Zhang et al. (2021) has shown that high-speed switching devices such as SIC and GAN reduce switching losses and improve overall efficiency.

Thermal Management: Effective cooling mechanisms, including heat sinks and liquid cooling, are crucial for preventing overheating, which can damage inverter components and reduce efficiency (Hassan et al., 2020).

Power Factor: The inverter’s ability to maintain a high power factor ensures efficient power delivery and minimizes losses in AC transmission (Li & Zhang, 2019).

Harmonics: Harmonics in the AC output can cause issues for sensitive equipment. Advanced modulation techniques, such as space vector PWM, are used to minimize harmonic distortion and improve the quality of the output waveform (Sharma & Pandey, 2018).

Load Regulation: An inverter's ability to maintain a stable output voltage under varying loads is crucial for consistent power supply. Good load regulation minimizes performance loss during fluctuations in demand (Jain & Sharma, 2020).

CHAPTER THREE

3.0	METHODOLOGY

This chapter discusses the method used in the design and construction of the 3KVA inverter system powered by a 24V battery. The inverter topology adopted is a Modified Sine Wave Inverter, chosen for its cost-effectiveness, simplicity, and sufficient performance for most household appliances.

  - MATERIALS USED

Inverter Board, Transformer (DC 24volt input), Buzzer, MOSFETS, IC Integrated Circuit, Capacitors, Diode, DC fuse, NPN Transistor, Indicator/LED, Voltmeter, DC Extractor fan (2pieces), Power switch , AC output socket, PV Cell, Battery Terminal, Housing case, DC cables, Charging Controller Board, LED Display Screen and Battery cell.

3.2	DESCRIPTION OF MATERIALS

- Inverter Board: Acts as the main control and switching circuit where all electronic components like MOSFETs, ICs, and resistors are soldered. It manages signal generation and power conversion.

- Fig 3.1:  image of an inverter board

- Transformer (DC 24V Input)

Converts the low-voltage (24V) DC from the battery into high-voltage (220V) AC output using electromagnetic induction.

Fig 3.2: image of a transformer

Buzzer: Provides an audible alert for conditions like low battery, overload, or fault warnings.

- MOSFET: Metal-Oxide-Semiconductor Field-Effect Transistor: Used as high-speed switches to convert DC to AC via high-frequency switching in the inverter circuit.

Fig 3.3: image of a MOSFET

- IC (Integrated Circuit): Likely used for generating PWM signals, timing control, and protection functions. Common examples include SG3525, TL494, or NE555.

Fig 3.4: image of an Integrated Circuit

- Capacitors: Input Capacitor (35V): Smooth out input voltage from the battery to reduce ripples before switching Output Capacitor (400V): Helps filter and stabilize the high-voltage AC output. Diodes: Ensure current flows in one direction only, preventing reverse current that could damage components. Also used in feedback, protection, and rectification.

- 8DC Fuse: Provides overcurrent protection by breaking the circuit when current exceeds 30 amps, preventing damage and fire hazards.

- NPN Transistors: Act as signal amplifiers or switching devices in the driver stage of the inverter circuit.

- Indicator / LED: Shows system status like power ON, charging, full charge, overload, or fault.

- Volt Meter: Displays the real-time voltage of either the battery or the inverter output to monitor system performance.

Fig 3.5: image of a volt meter

DC Extractor Fans (2 pieces): Used for active cooling of the inverter, preventing overheating of MOSFETs and other 3heat-sensitive components.

Fig 3.6: image of DC extractor fan

- Power Switch: Manually turns the inverter ON or OFF by connecting or disconnecting the battery or AC output.Provides a safe connection point to plug in AC appliances powered by the inverter.

- Fig 3.7: image of a power switch

- Housing Case: Encloses and protects the inverter's internal components from environmental damage and accidental contact.

Fig 3.8: image of a housing case

- 4mm Cable: Used for control and signal connections or low-current DC paths.

10mm Cable: Used for high-current DC paths, such as battery to MOSFETs or transformer.

Fig 3.9: image of a 4mm Cable

- PV Photovoltaic Cell Male and Female Connectors: These are solar panel connectors for connecting solar input to the inverter for charging the battery via a charge controller.

- Flat Diode: Likely used for protection or rectification in the charger or feedback sections. Helps manage voltage direction and polarity.

- Battery Terminal: Connects the 24V battery to the inverter system securely, ensuring stable power transfer.

- Charging Controller Board (P–N Junction): Manages the charging of the 24V battery from a solar panel, ensuring safe voltage and current regulation.

Fig 3.1.1: image of a Charging controller board

LED Display Screen (7/4 cm²): Displays important system parameters such as voltage, current, battery level, or error codes.

Fig 3.1.2: image of a LED display screen

3.2 Block Diagram of the Inverter

The major blocks in the system are:

- 24V Battery Supply: This is the primary DC power source for the inverter. It provides a stable 24-volt direct current needed to power the inverter circuit and convert DC to AC.

- Oscillator Circuit: Generates a stable and continuous square wave signal at a specific frequency (usually 50Hz or 60Hz) which sets the operating frequency of the inverter.

- Pulse Width Modulation (PWM) Generator: Produces PWM signals that control the switching behavior of the MOSFETs to efficiently convert DC to AC while controlling output voltage and waveform quality.

- Driver/Amplifier Stage: Amplifies the low-power PWM signals from the generator to the necessary voltage and current levels required to switch the MOSFETs effectively

- MOSFET Switching Stage: Acts as high-speed electronic switches, turning the DC voltage on and off in a controlled manner according to the PWM signals, thus creating a modified AC waveform.

- Step-up Transformer: Steps up the low-voltage AC output from the MOSFETs to the desired higher AC voltage (e.g., 220V or 110V) suitable for household or industrial loads.

- Output Filtering Stage (Optional): Smoothens and filters the inverter’s output waveform to reduce harmonics and produce a cleaner AC supply closer to a pure sine wave, improving compatibility with sensitive devices.

CHAPTER FOUR

4.0	SYSTEM CONSTRUCTION AND TESTING

4.1	TESTING AND EVALUATION UNDER LOAD CONDITION

The constructed 3KVA inverter was tested under various load conditions to evaluate its performance and stability. The testing involved connecting the inverter to a 24V battery bank and gradually applying electrical loads, starting from light appliances such as energy-saving bulbs and fans, up to heavier loads like a refrigerator and electric pressing iron. Throughout the testing, the output voltage remained stable around 220V AC, and the frequency stayed close to 50Hz. The inverter operated efficiently under partial and full loads, with only moderate heating observed in the transformer and MOSFETs during prolonged high-load operation. Adequate ventilation and heat sinks helped maintain safe temperatures. Overall, the inverter performed reliably within its rated capacity, making it suitable for household or office use.

4.2	POWER RATING

The power rating of the inverter defines its maximum load-handling capacity and determines the types of appliances it can support. In this project, the inverter was designed with a power rating of 3KVA (3000VA), which corresponds to a maximum power output of approximately 2400 watts, assuming a power factor of 0.8. This rating indicates that the inverter can effectively power a combination of household or office appliances such as fans, televisions, lighting systems, laptops, and refrigerators, provided the total load does not exceed its rated capacity. The system operates using a 24V DC battery input, which is stepped up to 220V AC output, making it suitable for standard electrical devices. Careful consideration was given to component selection including transformer size, wire gauge, and switching devices to ensure the system could consistently deliver the rated power without overheating or voltage drops.

4.3	DESIGN SPECIFICATIONS

The inverter was designed to produce a modified sine wave output, which is a stepped approximation of a pure sine wave, suitable for most household appliances. Unlike a smooth sine wave, the modified sine wave consists of a square-like waveform that changes polarity with a short zero-voltage pause between cycles, reducing harmonic distortion compared to a pure square wave. This waveform is easier and cheaper to generate using basic oscillator and switching circuits, making it ideal for low to medium-cost inverter systems. The output frequency was maintained at approximately 50Hz, and the RMS voltage was kept close to 220V AC. This design allows compatibility with common appliances like lights, fans, and chargers, though sensitive electronics may require a pure sine wave inverter for optimal performance. Below is the graphical representation of the modified sine wave produced by the inverter:

Fig 4.1: image of a waveform

4.4	CHALLENGES ENCOUNTERED

During the design and construction of the 3KVA solar inverter using a 24V battery, several challenges were encountered that affected the development process. One major challenge was ensuring the stability of the oscillator circuit, as slight variations in frequency affected the output waveform quality. Another issue was heat generation in the MOSFETs and transformer during extended high-load testing, which required the addition of larger heat sinks and improved ventilation. Component sourcing also posed difficulties, especially in obtaining high-current-rated MOSFETs and transformers suitable for 3KVA operation. Additionally, achieving consistent output voltage under varying load conditions required careful calibration of the control circuit. Despite these setbacks, adjustments and redesigns were implemented to overcome the issues and ensure reliable inverter performance.

4.5	PROTECTION AND SAFETY FEATURES

To ensure reliable and safe operation of the 3KVA solar inverter, several protection and safety features were integrated into the design. A fuse was included at the input stage to prevent damage from overcurrent or short circuits, while reverse polarity protection diodes were used to safeguard against incorrect battery connections. Cooling fan were installed to manage thermal buildup in the MOSFETs and transformer, reducing the risk of overheating.

Additionally, the system was designed with overload protection, which automatically shuts down the inverter when the connected load exceeds its rated capacity. Proper insulation, spacing of high-voltage components, and a metallic casing were also employed to prevent electrical shocks and ensure user safety. These features collectively enhance the durability and safe functioning of the inverter system under various operating conditions.

CHAPTER FIVE

5.0	RESULTS, CONCLUSION, AND RECOMMENDATIONS

5.1	SUMMARY OF FINDINGS

The design and construction of a 3KVA solar inverter using a 24V battery system were successfully carried out. The system was able to convert 24V DC from the battery into a stable 220V AC output suitable for powering basic household appliances such as light bulbs, fans, and televisions. During testing, the inverter performed efficiently under different load conditions and maintained a consistent output voltage and frequency. The circuit components worked as expected, and the protection features, including low battery cut-off, overload, and short-circuit protection, were effective in preventing damage. Heat sinks and cooling fans were also tested and functioned well in managing the system’s temperature during extended use. Overall, the system demonstrated good performance in terms of reliability, safety, and efficiency. The use of simulation before construction helped to reduce errors and ensure the success of the physical build.

5.2	RESULT ANALYSIS

After the construction of the 3KVA solar inverter system, several tests were carried out to evaluate its performance. The inverter was connected to a fully charged 24V battery bank, and its output was measured using a multimeter and oscilloscope to verify voltage, frequency, and waveform characteristics. The system successfully produced an output voltage of approximately 220V AC at 50Hz, which meets the standard requirement for household appliances. The inverter was tested with different loads such as light bulbs, standing fans, and a small refrigerator. It handled these loads efficiently without overheating or shutting down, showing that the system could sustain a power output close to 3KVA. The protection features were also tested. When a load greater than the rated capacity was applied, the inverter automatically shut down to prevent damage, confirming the functionality of the overload protection circuit. The low battery protection was also triggered when the battery voltage dropped below the safe level, preventing deep discharge. The inverter efficiency was estimated to be between 80% and 85%, which is acceptable for a locally built inverter. Minor voltage drops were observed under heavy load, which is typical for modified sine wave inverters. The heat sinks and cooling fans were effective in controlling temperature during prolonged use.

5.3	CONCLUSION

This project successfully demonstrated the design and construction of a 3KVA solar inverter system using a 24V battery. The inverter was able to convert DC power from the battery into a stable 220V AC output suitable for powering household appliances. The system was tested under various load conditions and showed reliable performance, with built-in protection features functioning as expected. The project proves that with proper planning, affordable components, and a clear understanding of power electronics, a cost-effective and efficient solar inverter system can be built locally. It offers a practical solution to the problem of unstable electricity supply, especially in areas where access to the national grid is limited or unreliable.

5.4	RECOMMENDATION FOR IMPROVEMENT

While the 3KVA solar inverter system performed successfully, there are several ways it can be improved for better efficiency, durability, and user experience:

Use of Pure Sine Wave Inverter Topology: The current design may use a modified sine wave, which is less ideal for sensitive electronics. Switching to a pure sine wave inverter would ensure compatibility with all appliances and reduce noise or overheating in some devices.

Incorporation of MPPT Charge Controller: Replacing the basic charge controller with a Maximum Power Point Tracking (MPPT) controller would significantly improve the efficiency of solar charging by extracting more power from the solar panels, especially under varying sunlight conditions.

Improved Battery Technology: Using lithium-ion batteries instead of traditional lead-acid batteries would increase the system’s lifespan, reduce maintenance needs, and allow deeper discharge without damaging the battery.

Digital Monitoring System: Adding a digital display or monitoring system (e.g., LCD screen or mobile app) would allow users to track important parameters such as battery level, load status, and fault warnings in real time.

Compact and Modular Design: Future versions of the system can be made more compact and modular for easier transportation, installation, and repair. This would make the product more user-friendly and commercially viable.

Enhanced Protection Features: Additional safety measures like surge protection, reverse polarity protection, and thermal shutdown should be considered to increase reliability and user safety.

5.5	FUTURE WORK

Future advancements in the design and functionality of the 3KVA solar inverter system can focus on several key areas to enhance performance, efficiency, and adaptability to diverse energy needs:

- Integration with Smart Grid Systems: Future versions can be designed to interface with smart grid infrastructures, allowing for bi-directional power flow and intelligent load management, which would support grid-tied and hybrid applications.

- Hybrid Energy Input Support: The inverter can be modified to accept multiple energy inputs, such as wind, hydro, or diesel generators in addition to solar, to ensure consistent power availability in varying environmental conditions.

- Artificial Intelligence (AI) Integration: Employing AI algorithms can help in predictive energy management, fault detection, and adaptive control based on usage patterns and weather conditions, improving overall system intelligence and reliability.

- Scalability for Industrial Use: The inverter system can be scaled up to higher capacities (e.g., 5KVA or 10KVA) for industrial or community-based solar applications, incorporating more robust components and power management strategies.

REFERENCES

Akinboro,F. G., Sanusi, A. A., & Oladosu, D. A. (2012). Design and construction of a modified sine wave inverter. International Journal of Engineering and Technology, 2(4), 643–650.

Balogun, A. O., Adedokun, O. A., & Aladejana, J. A. (2013). Comparative analysis of inverter types and their applications. Journal of Electrical Engineering, 5(2), 45–51.

Esram,	 T., & Chapman, P. L. (2007). Comparison of photovoltaic array maximum power point tracking techniques. IEEE Transactions on Energy Conversion, 22(2), 439–449.

Gupta,	 A., Gupta, M., & Arora, S. (2011). Design and development of intelligent control system for inverter used in solar applications. International Journal of Advanced Engineering Technology, 2(4), 379–383.

Ikejuba,D. C., & Akande, A. (2016). Design and development of a solar power inverter system for rural applications. Nigerian Journal of Technology, 35(3), 526–531.

Luo, 	X., Wang, J., Dooner, M., & Clarke, J. (2015). Overview of current development in electrical energy storage technologies and the application potential in power system operation. Applied Energy, 137, 511–536.

Nema,	 P., Nema, R. K., & Rangnekar, S. (2009). A current and future state of art development of hybrid energy system using wind and PV-solar: A review. Renewable and Sustainable Energy Reviews, 13(8), 2096–2103.

Ohunakin, O. S., Adaramola, M. S., Oyewola, O. M., & Fagbenle, R. O. (2014). Solar energy applications and development in Nigeria: Drivers and barriers. Renewable and Sustainable Energy Reviews, 32, 294–301.

Oseni, 	M. O. (2012). Improving households’ access to electricity and energy consumption pattern in Nigeria: Renewable energy alternative. Renewable and Sustainable Energy Reviews, 16(6), 3967–3974.

APPENDICES

"Design and Construction of a 3KVA Solar Inverter Using 24V Battery". This section includes supplementary materials that support the content of your main chapters.

Appendix A: Circuit Diagram of the 3KVA Solar Inverter

- Detailed schematic diagram showing the inverter circuit including:

  - Oscillator stage

  - Driver stage

  - Power transistor/MOSFET stage

  - Transformer interface

  - Output filter

Appendix B: Components List

| Component | Quantity | Specification |
| --- | --- | --- |
| MOSFET (IRF3205) | 8 | 55V, 110A |
| Transformer | 1 | 24V–0–24V to 220V, 3KVA |
| PWM Controller (SG3525) | 1 | 16-pin DIP |
| Capacitors | 10 | 470μF, 100V Electrolytic |
| Resistors | 15 | Various (1kΩ, 10kΩ, etc.) |
| Heat Sink | 2 | Aluminum, large size |
| Diodes (1N5408) | 4 | 3A, 1000V |
| Relay | 1 | 24V, 30A |
| Cooling Fan | 1 | 12V DC |
| PCB Board | 1 | Standard Vero board |

Appendix C: Inverter Testing Results

| Test Load | Voltage Output | Frequency | Observation |
| --- | --- | --- | --- |
| 100W bulb | 220V | 50Hz | Stable |
| 500W Fan | 219V | 50Hz | Slight drop |
| 1000W Load | 218V | 50Hz | Moderate heating |
| 2500W Load | 215V | 50Hz | Near full capacity |
| 3000W Load | 212V | 50Hz | Max limit reached, fan activates |

Appendix D: PCB Layout

- Layout showing the arrangement of key components on the printed circuit board (PCB).

- Labeling of input/output terminals, MOSFETs, controller IC, etc.

Appendix E: Project Pictures

- Step-by-step images showing the construction stages:

  - Initial circuit assembly

  - Soldering process

  - Enclosure and final build

  - Test setup